UDK 614.844

V.A. Dureev, candidate of technical sciences, associate professor of NUCD of Ukraine

MATHEMATICAL MODEL OF THERMAL FIRE DETECTOR WITH THE THERMISTOR

(presented by Doctor of technical sciences					)

The article presents the results of research of thermistor design, composition and nominal resistance influence on dynamic parameters of thermal fire detector.

Key words: fire detector, sensitive element, thermistor, dynamic equation, dynamic parameter, time constant.

Description of the problem.  Fire detectors (FD) constitute the important part of modern fire alarm systems (FAS), documentation for which does not always contain their main technical data. Research of FD operation efficiency demands information on technical data of their components, in particular dynamic parameters of sensitive element (SE).

Dynamic parameters (FD) can be determined by using of detector mathematical model which considers the material of semiconductor, constructive design and range of operating temperatures. Accordingly there is a problem of technical data improvement of FAS elements dynamic parameters.

Analysis of latest investigations and publications. In [1, 2] the models of SE point thermal FD are suggested considering constructive characteristics and conditions of fire expansion. However, proposed models demand precise mathematical description of SE and additional experimental data of the researched FD. In [3] there is the model of SE with posistor without considering the design and in [4] the model of SE with thermistor which takes into consideration the constructive peculiarities of SE. According to [4], dependence of thermistor resistance RT on temperature, considering the material of semiconductor and design peculiarities of thermistor is:

,				(1)

where A, b, B – are constant that depend on composition of thermistor semiconductor material and sensitive element design; T – current thermistor temperature, K.

In [5] for simplifying of engineering calculations under b <<1 it was accepted that constant A corresponds to thermistor resistance R∞ under infinitely high temperature. At this in order to increase the precision and for convenience of RT determination it is suggested to take into consideration the nominal resistance:

,				(2)

where RН – thermistor nominal resistance, Om, under the temperature ТН, K.

Approach for determination of FD dynamic parameters according to test data is presented in [6].

Aims and solutions. This work is aimed on research of total influence of thermistor semiconductor material, SE design peculiarities and its nominal resistance under set temperature on the FD dynamic parameters. Let’s perform mathematical description of FD with thermistor in the interval of working temperatures taking into account the SE design peculiarities, semiconductor material and its nominal resistance under set temperature. Equation (1) considering (2) has the following view;

.			(3)

Let’s compare differentials of the left and right part:

;		 (4)

;	 (5)

;	 (6)

;   	 ,		 (7)

where Rt – thermistor resistance under nominal temperature, Om; β – temperature coefficient.

Mathematical model of thermistor, as dynamic chain, is obtained from equation for non-stationary thermal exchange under criteria Bio < 0,1 that corresponds to even distribution of temperature inside SE.

Quantity of heat transferred and absorbed by thermistor [4]:

,			(8)

where C – thermistor material heat capacity, J∙kg-1∙К-1; m – thermistor mass, kg; T – thermistor temperature, K; τ – hour, sec; α – coefficient of convection thermal exchange, W∙м-2∙К-1; F – thermistor surface square, м2; ТВ – environment temperature, K.

Let’s insert (6) into (8) and get:

. 	(9)

In the result of research, after linearization (9) by the method of full differential the FD dynamic equation was obtained, which considers the overall impact of thermistor semiconductor material, SE design peculiarities and nominal resistance:

;				(10)

;  , 		(11)

where ТТ – thermistor time constant, sec; КТ – thermistor amplification coefficient; ,  – relative variables.

According to [6]. The FD time constant ТТ is determined by formula:

,			 (12)

where t1 – FD trigger temperature for the programmed temperature growth speed, K; tstat – static temperature of FD trigger, K;  – programmed temperature change speed [K/ sec].

Analysis of the obtained results demonstrates that in order to decrease the FD inertia, mass should be decreased and SE square increased.  In order to improve the convective thermal exchange, plate radiator should be placed on SE.

Conclusions. FD dynamics equation was obtained considering the overall influence of thermistor semiconductor material, SE design peculiarities and its nominal resistance. In order to decrease FD inertia mass should be decreased and SE square increased.

LITERATURE

1. Абрамов Ю.А. Модель теплового пожарного извещателя и оценка времени его срабатывания/ Ю.А. Абрамов, Ю.Ю. Переста// Проблемы пожарной безопасности. – Х.: ХИПБ. – 1997. – С.53 – 57.

2. Гвоздь В.М. Терморезисторные тепловые пожарные извещатели с улучшенными характеристиками и методы их температурных испытаний. Дисс. канд. техн. наук: 21.06.02 – Черкассы. – 2005. –181с.

3. Дуреев В.А. Математическое описание чувствительного элемента максимального теплового пожарного извещателя с терморезистором / В.А. Дуреев, А.Н. Литвяк // Проблемы пожарной безопасности. – Х.: НУГЗУ. – 2012. № 32 – С. 74–77. Режим доступу: http://nuczu.edu.ua/sciencearchive/ProblemsOfFireSafety/vol32/dureev.pdf

4. Дуреев В.А. Математическая модель чувствительного элемента теплового пожарного извещателя с термистором // Проблемы пожарной безопасности. – Х.: НУГЗУ. – 2016. Випуск 40 – С. 90–93.  Режим доступу:

http://nuczu.edu.ua/sciencearchive/ProblemsOfFireSafety/vol40/dureev.pdf

5. Шашков А.Г. Динамические свойства цепей с термисторами/ А.Г. Шашков, А.С. Касперович // –М.– Л.:Госэнергоиздат.–1961.–208с.

6. Дуреев В.А. Определение постоянной времени теплового пожарного извещателя с термистором // Проблемы пожарной безопасности. – Х.: НУГЗУ. – 2017. Випуск 41 – С. 70–73.  Режим доступу:

http://nuczu.edu.ua/sciencearchive/ProblemsOfFireSafety/vol41/dureev.pdf

В.А Дуреев

Математическая модель теплового пожарного извещателя с термистором

Представленные результаты исследования влияния конструктивных особенностей, состава и номинального сопротивления термистора на динамические параметры теплового пожарного извещателя.

Ключевые слова: пожарный извещатель, чувствительный элемент, термистор, уравнение динамики, динамический параметр, постоянная времени.

V. A. Dureev

А mathematical model of thermal fire detector with the thermistor.

Presented results of research of influence of structural features, composition and nominal resistance of termistor on the dynamic parameters of thermal fire detector.

Keywords: fire detector, sensitive element, the thermistor, the dynamic equation, the dynamic parameter time constant.